Guidelines for LPG Environmental Policy & Approvals Unit Page 1 of 3 trim://09/45644 Permanently connected LPG cylinders Introduction Liquid petroleum gas (LPG) is a heavier than air flammable gas that is a Class 2.1.1A hazardous substance under the Hazardous Substances and New Organisms Act 1996 (HSNO). This guideline is in response to numerous enquiries about the safe handling and storage of LPG in compliance with the following legislation, approved standards and the Christchurch City Plan: • Hazardous Substances (Classes 1-5 Controls) Regulations and DGTN No. 35 • NZS 5261:2003 Gas Installation • AS/NZS 1596:2002 • Christchurch City Plan. Requirements and recommendations These can be split arbitrarily into the following storage quantities; for consideration under the different regulatory requirements: • Under 15kg • Between 15kg – 100kg • Between 100kg – 300kg • Over 300kg. Under 15kg By right you can have 1 x 9kg cylinder inside a building. But it is recommended wherever possible cylinders are stored outside. In the event of a gas leak at the cylinder this means the gas is more easily dispersed. The installation of 9kg cylinders for supply of hobs shall be in accordance with NZS 5261:2003. Where possible the LPG cylinder should be stored outside and piped in to the appliance. If it has to be inside the following requirements shall be followed: (a) The cylinder connection system shall be suitable for indoor use, i.e. any regulator should be suitable for indoor use. (b) Cylinders shall not be more than 25 litres water capacity (9kg cylinder). (c) The cylinder shall not be in the same compartment as a power point or electrical appliance, for example waste disposal or dishwasher. (d) The compartment in which the cylinder is located, shall be ventilated to the outside with minimum apertures being 20mm x 1m for each cylinder-top and bottom of cupboard. It is recommended that a qualified gasfitter carries out the installation of 9kg gas hob systems. Gasfitters are only legally required to certify installations over 15kg. Guidelines for LPG…Continued 15 – 100kg These installations normally consist of 2 x 45kg cylinders (“2 pack”). They shall be located on the outside of the building or separate from the building openings as shown in Figure 1. Figure 1: Isolation distances around Class 2.1.1A exchange cylinder (up to 100kg). They must be installed in accordance with NZS 5261:2003 by a qualified gasfitter. The full system installation must be certified by a craftsman gasfitter prior to commissioning. Cylinder stores less than 100kg do not require HSNO test certification however they still have to comply with the relevant HSNO legislation and NZS 5261:2003. Between 100kg – 300kg Where gas usage requires on-site storage greater than 100kg the installation requires: • Certification from a craftsman gasfitter • Location Test Certification from an Environmental Risk Management Authority (ERMA) approved HSNO Test Certifier • Approved Handler • Secured storage. The gas providers are normally the Approved Handlers for the store and will require confirmation that the store has been issued with a Location Test Certificate before they can leave cylinders on the premises. If the hazardous substance (LPG) is not considered secure or storage is non-complying under HSNO, they should not leave cylinders until the non-compliance has been rectified. Environmental Policy & Approvals Unit The cylinder store can be against a building as long as the building is constructed from fire-resisting materials behind and 2 metres either side of the cylinders. (ERMA accept sheet iron as providing adequate “fire resistance” in this situation.) Refer to Figure 2 for siting. Figure 2: Isolation distances around Class 2.1.1A exchange cylinder (greater than 100kg) Greater than 300kg In addition to the requirements for greater than 100kg as shown above, the Christchurch City Plan must be complied with. For residential zones the storage of LPG in excess of 300kg will require resource consent. A resource consent information pack can be obtained from the Environmental Policy and Approvals Unit at the Council. Separation from Ignition sources Cylinders should be installed with clearances given below from sources of ignition, e.g. electrical equipment and be at least 1 metre from readily ignitable material. Figure 3: Hazardous atmosphere zone around Class 2.1.1A exchange cylinder Summary <15kg; 15–99.9kg; 100– 299.9kg; >300kg. Resource consent; X; X; X; . HSNO Location Certificate; X; X; ; . Gas Fitters Certificate; X; ; ; . Test Certification ERMA provides a list of approved Test Certifiers who can advise on compliance and issue Hazardous Substances Location (HSL) test certification (www.ermanz.govt.nz). Who to contact – Test Certifiers Further information can be obtained from Tony Neilson or Brendan Haughian Phone 06 343 1860 – office or Tony mobile 027 443 6938 and Brendan 027 664 2030 Email – tony@envirohaz.co.nz or brendan@envirohaz.co.nz

http://resources.ccc.govt.nz/files/GuidelinesForResidentialLPG-docs.pdf