Underground tanks at Service Stations and pipework and tank removal

Stationary Container Systems at Service Stations Description of a stationary container system A stationary container system means a stationary tank and its associated equipment, pipework, and fittings up to and including the dispensers. Where LPG is stored, the pumps, cylinder-filling equipment, and, for large tanks, any fire-fighting systems are part of the stationary container system. The certification process verifies that the system has been designed and installed and is operated in accordance with accepted engineering principles. Threshold quantities Stationary container systems that contain a hazardous substance above the threshold quantity must have a stationary container system test certificate (see Table 1). At service stations, this typically applies to petrol, diesel and LPG stationary container systems. Table 1: Stationary container system test certificate threshold quantities Substance Container location Threshold quantity Petrol (new)* Above ground > 2,500 L Below ground Any volume Petrol (existing)** Above ground > 2,500 L Below ground > 5,000 L LPG Above ground Any volume Below ground Any volume Diesel Above ground > 5,000 L Below ground Any volume * Stationary container system constructed on or after 1 April 2004. ** Stationary container systems constructed before 1 April 2004. Maintain records Keep records detailing the standards to which all components of a stationary container system were designed and installed, as well as service records. These records may be in the form of drawings, a test certifier’s report, or a design report. For existing stationary container systems, get and keep as many details as possible. An equipment register will help you to maintain up-to-date records.. Person in charge is responsible The person in charge is responsible for ensuring the stationary container system test certificate is obtained, even when the service station owner does not own the stationary container system (for example, the fuel supplier or another party owns and is responsible for them). No test certificate If a stationary container system does not have a test certificate, hazardous substances must not be put into it. Test certifiers issue test certificates To obtain a stationary container system test certificate, contact a test certifier approved by ERMA New Zealand. The test certifier will need to visit your service station and assess the stationary container system before he or she can issue a test certificate. A register of test certifiers is on the ERMA New Zealand website (http://www.ermanz.govt.nz/search/tc.html). Stationary container system certification For a stationary container system to be certified, a test certifier will assess (as applicable) and verify:1 • the system’s design, construction and installation • the pressure management and emergency pressure management system • liquid level indicators • lightning protection (above ground stationary tanks) • the distances between stationary containers, tank wagons and transfer points • fire-fighting systems (above ground stationary tanks) • secondary containment systems • markings • maintenance carried out • pipework and fittings • dispensers. 1 Schedule 8 of the Hazardous Substances (Dangerous Goods and Scheduled Toxic Substances) Transfer Notice 2004 (as amended) (http://www.ermanz.govt.nz/hs/transfer/docs.html) Certification of secondary containment system Secondary containment systems are required for stationary containers. If the stationary container is: • storing diesel, or • is storing petrol and has an integral secondary containment system (that is, it is a double skin tank) the certification of the secondary containment system is part of the stationary container test certificate. If the secondary container system is storing petrol and it is a single skin tank, the certification of the secondary containment system is part of the location test certificate. LPG stationary container system For an LPG stationary container system, the hardware is certificated under the Health and Safety in Employment (Pressure Equipment, Cranes, and Passenger Ropeways) Regulations 1999. This reduces the documentation requirements required by the regulations under the HSNO Act for a stationary container system test certificate. To obtain certification under the Health and Safety in Employment (Pressure Equipment, Cranes, and Passenger Ropeways) Regulations 1999, see Pressure Equipment, Cranes, and Passenger Ropeways Regulations 1999: A general guide to the Health and Safety in Employment on the Department of Labour website (http://www.osh.govt.nz/order/catalogue/354.shtml). Dispensers Petrol and LPG dispensers must be of approved types. Markings Stationary tanks must be marked with identifying information about their design and construction. Pipework connected to an above-ground stationary tank must be marked (with colour coding) if the capacity of the stationary tank is more than: • 12,000 L of LPG, or • 60,000 L of petrol or diesel. It is good practice to mark vent pipes of below ground stationary tanks to identify the stationary tanks they are connected to. Existing stationary container systems Not all stationary container systems constructed before 1 April 2004 will comply with the requirements. If they have a capacity no greater than 60,000 L, you may manage them under an ERMA New Zealand approved code of practice.2 For stationary container systems encompassed by a code of practice, there are alternatives to secondary containment systems. These require management procedures that incorporate activities such as routine stock reconciliation and periodic checks of observation wells or integrity testing. Compliance plans for existing stationary container systems If a stationary container system constructed before 1 April 2004 does not comply with the requirements or an approved code of practice, you may submit a compliance plan application to ERMA New Zealand. This compliance plan must be submitted before 31 March 2008 and it must be endorsed by a test certifier. It must detail how, and the time within which, the stationary container system or the operational procedures applying to it will be altered so they comply. File your compliance plan and the letter of approval in Appendix 4, or file the plan and letter elsewhere and record their location in section 15. Remove disused belowground stationary tanks If your service station stops using a below-ground tank for more than three months, you must. • have the stationary tank removed, or • get ERMA New Zealand’s permission to leave the tank in place. ERMA New Zealand may allow the tank to remain for valid reasons, for example, if it is under a building and cannot be removed without destroying the building. 2 Code of Practice for the Management of Existing Stationary Container Systems up to 60,000 Litre Capacity (http://www.ermanz.govt.nz/hs/compliance/codesofpractice.html). The following links provide more information: http://www.ermanz.govt.nz/resources/publications/pdfs/Web%20Stationary%20Container%20Systems.pdf http://www.ermanz.govt.nz/news-events/focus/upss-draft2002.pdf

Code of Practice for the DESIGN, INSTALLATION AND OPERATION OF UNDERGROUND PETROLEUM STORAGE SYSTEMS

INTRODUCTION This Code of Practice has been prepared as a statement, both of policy and of specific measures to be taken, to ensure safe and efficient storage of petroleum products in underground petroleum storage systems UPSS, for the protection of people, property, and the environment. This code is an update of the code first published in 1992 and incorporates the additional information published in 1995 as Supplement No.1 Management Of Existing Underground Petroleum Storage systems. It also reflects changes in technology and experience gained since the publishing of the original code. The Code is intended to be read in conjunction with, and to complement, the Hazardous Substances and New Organisms Act 1996 and the Resource Management Act. It does not replace or supersede the requirements of the Acts or Regulations but provides guidance on how they can be met, and at the same time the environment can be protected from the potential hazards of petroleum product leakage. It is not intended to be used as a technical specification. It must be supported by detailed technical documentation to obtain approval for any project work from a licensing authority. The Code defines requirements for the storage of hydrocarbon products underground, and states specifically and in detail how these facilities and the individual items therein shall be designed, fabricated, installed, commissioned and operated. The Code will be reviewed from time to time as the requirements of society change and available technology improves. Such reviews should be undertaken at least every five years by the representatives of all those who have contributed to its preparation. SUMMARY The handling of petroleum products has always involved risk. The hazardous nature of the products handled and the serious potential consequences of system failure have required the oil industry to become highly accomplished in the management of this risk to a level at which the probability of system failure is acceptably remote. One of the first principles in handling hydrocarbon fuels is to keep the product within the system. The primary concern is to maintain and operate the system to ensure that at all times the product is contained. The consequences of system failure may then be regarded as the result of exceptional circumstances rather than a hazard associated with normal operation. Following is the detailed link with further information: http://www.ermanz.govt.nz/news-events/focus/upss-draft2002.pdf

Code of Practice for Pipework Marking for Class 3.1 Flammable Liquid Fuels in Storage Depots

ERMA NEW ZEALAND INFORMATION SHEET Code of Practice HSNOCOP 21-1 NUMBER 46 August 2007 Codes of Practice: What are they and what is their significance? Codes of Practice are able to be approved by the Authority under Sections 78 and 79 of the HSNO Act. In practice they are approved by the ERMA New Zealand Chief Executive under delegated authority. Codes of Practice are “how to” documents. They tell you how you can meet the requirements of the HSNO regulations and controls in a way that is legally defensible. Also, where provided for in the legislation, they may introduce requirements (such as recognised standards) that are in addition to those specified in the legislation. However, they are not mandatory! If you have other ways of meeting the requirements then you can adopt those instead. Most Codes will be developed by industry or user groups rather than by ERMA New Zealand. Where can you get a copy of this Code? Code HSNOCOP 21-1 was developed by ERMA New Zealand. A hard copy of the Code will be held at ERMA New Zealand’s reception in our Wellington Office. You can inspect a copy there. It is also available on the ERMA New Zealand website: www.ermanz.govt.nz What is this Code about? The purpose of this Code of Practice - Pipework Marking for Class 3.1 Flammable Liquid Fuels in Storage Depots - is to provide a means of compliance with the requirements of clause 79(2)(b) of Schedule 8 to the Hazardous Substances (Dangerous Goods and Scheduled Toxic Substances) Transfer Notice 2004 (as amended). This Code is intended to be applied to existing fuel storage depots to allow continuation of existing practice without the need to obtain approval for a compliance plan. However, it can also be used for new installations to avoid differing standards for marking at the same facility. ER-IS-46-01 08/07 What is in the Code? It is not possible to give a full summary of the Code in this Information Sheet, but the following information will give you a good indication of what is covered in the Code. Content The Code covers the following areas for pipework marking: 􀂃 Location of markers. 􀂃 Colour of markers. 􀂃 Design of markers. 􀂃 Small pipe identification tags. 􀂃 Function markers. Limitation This Code is only applicable to pipework connected to an above ground stationary tank in a stationary container system and does not cover: 􀂃 Pipelines outside a fuel storage depot boundary. 􀂃 Underground tanks. 􀂃 Pipework to which the Health and Safety in Employment (Pressure Equipment, Cranes and Passenger Ropeways) Regulations 1999 (PECPR) applies. 􀂃 Pipework to which the Health and Safety in Employment (Pipelines) Regulations 1999 applies. The Code also covers marking of pipework that is not covered by the HSNO legislation. In such cases the information is provided on an advisory basis only, but will provide one source of information for users. Conclusion This paper has been prepared by ERMA New Zealand to help you decide whether this Code would be of relevance to you. It is not in itself a Code of Practice. Further information or feedback For information on hazardous substances compliance visit -www.ermanz.govt.nz/hs/hscompliance.asp or call our Hazardous Substances Compliance Line on 0800 376 234. ERMA New Zealand PO Box 131 Wellington Tel: 04 916 2426 Email: hsinfo@ermanz.govt.nz Website: www.ermanz.govt.nz

The link to the above information:

http://www.ermanz.govt.nz/resources/publications/pdfs/ER-IS-46-1%2008%2007.pdf