- The Farming Industry:

STATIONARY CONTAINER TEST CERTIFICATES / HAZARDOUS SUBSTANCE LOCATION TEST CERTIFICATES

Who needs STATIONARY CONTAINER SYSTEM CERTIFICATES in the farming industry?

The following are the decisive factors:   Any tank, drum or container for petrol or diesel must –

be at least 6 metres from other dangerous goods or combustible materials; and

- be at least 20 metres from dwellings or other buildings made of combustible

- be compounded (bunded) or located so that any spillage will not endanger 
any building, or flow into any natural water body.

- And very importantly –

Must comply with the design, construction and installation requirements, materials and for -

| PETROL | Above ground tank |  | Below ground tank |  | Drums or Containers |
| --- | --- | --- | --- | --- | --- |
| Stationary Container Test Certificate | Up to 2,500 Litres | More than 2,500 Litres | Any Capacity |  |  |
| New tanks | No | Yes | Yes |  | Not required |
| Existing tanks Note 1. | No | Yes | Up to 5,000 Ltrs Note 2. | More than 5000 Ltrs |  |

- An Existing Tank is one installed and in use prior to 1 April 2004. Refer to Guidance for 
Storage of Petrol on Farms on the ERMA site ER-IS-41-1.pdf

- The tank must comply with the Code of Practice for Existing Stationary Container Systems 
up to 60,000 litres capacity. If in doubt check with a Test Certifier or competent person.

| DIESEL | Above ground tank |  | Below ground tank | Drums or Containers |
| --- | --- | --- | --- | --- |
| Stationary Container Test Certificate | Up to 5,000 Litres | More than 5,000 Litres | Any Capacity |  |
| New and existing tanks | No | Yes | Yes | Not required |

Who needs a HAZARDOUS SUBSTANCE LOCATION TEST CERTIFICATE (Location Test Certificate) in the Farming Industry?

| PETROL | Above ground tank |  | Below ground tank |  | Drums or Containers |  |
| --- | --- | --- | --- | --- | --- | --- |
| Location Test Certificate | Up to 2,500 Litres | More than 2,500 Litres | Any Capacity |  | Up to 2,000 Litres | More than 2,000 Litres |
|  | No | Yes | Yes |  | No | Yes |
| Existing tanks Note 1. | No | Yes | Up to 5,000 Ltrs Note 2. | More than 5000 Ltrs |  |  |
| DIESEL | Above ground tank |  | Below ground tank |  | Drums or Containers |  |
| Location Test Certificate | Not required |  |  |  | Not required |  |

Click the link below to view the Code of Practice/Approved Practice Guides:

APG for Safe Above-Ground Fuel Storage on Farms - HSNO Act 1996 
COP for Filling of Below Ground petrol Tanks by Pumping - HSNO Act 1996

Signage for fuel storage

All bulk fuel stored on your farm needs to have appropriate signage. Signs are required regardless of whether the fuel is stored in tanks, drums or any other type of container.

Signs ensure people are informed of hazards, can minimise risks and be aware of what to do if anything goes wrong.

When do I need signage?

You need to have signage on all bulk fuel tanks and where you have containers with more than:

• 250 litres of petrol or aviation gasoline;

• 1,000 litres of diesel or kerosene.

What are the requirements?

Signs need to be visible to people entering the area where the fuel is stored.

These signs tell people that the area contains petrol, diesel (or other fuels), outlines the hazards of these fuels and explains what must to be done to manage the hazards.

The signs must also inform people what to do in an emergency and who to contact. They will alert emergency services that fuel is present if they have to respond to deal with an emergency.

Health and Safety in Farming - HSNO brief for farmers –  Signage for fuels on farms

The information required on a sign can be in the form of pictures or words, and must be able to be read from 10 metres away and be understandable.

For fuel tanks, the signs on each tank (such as the examples overleaf) need to be at least 29 cm by 42 cm (A3) in size.

Further information

Best practice for fuel storage can be found in the Approved Practice Guide for Safe Above-Ground Fuel Storage on Farms, available from:

http://www.ermanz.govt.nz/resources/publications/pdfs/ER-APG-03-1.pdf

See also the New Zealand Chemical Industry Council Signage for Premises Storing Hazardous Substances and Dangerous Goods.

You should also check with your councils to see if they have any requirements in their District or Regional Plans.

Information is also available from the ERMA New Zealand Hazardous Substance Compliance Line 0800 376 234.

| Signage for Petrol | Signage for Diesel |
| --- | --- |